## Energy Storage Models
SunSpec Alliance
Energy Storage Information Models
2014-10-01
Draft 3
Last Updated October 26, 2015
This spreadsheet is a working draft of the SunSpec Alliance Energy Storage information model set. It is a companion to the "SunSpec Alliance Interoperability Specficiation - Energy Storage Models" which is currently at Draft 3 status. As such, neither of these documents is suitable for implementation at this time and are provided for review purposes only.
Copyright © SunSpec Alliance 2009-2015. All Rights Reserved. All other copyrights and trademarks are the property of their respective owners. License Agreement and Copyright Notice
This document and the information contained herein is provided on an "AS IS" basis and the SunSpec Alliance DISCLAIMS ALL WARRANTIES, EXPRESS OR IMPLIED, INCLUDING BUT NOT LIMITED TO ANY WARRANTY THAT THE USE OF THE INFORMATION HEREIN WILL NOT INFRINGE ANY OWNERSHIP RIGHTS OR ANY IMPLIED WARRANTIES OF MERCHANTABILITY OR FITNESS FOR A PARTICULAR PURPOSE. This document may be used, copied, and furnished to others, without restrictions of any kind, provided that this document itself may not be modified in anyway, except as needed by the SunSpec Technical Committee and as governed by the SunSpec IPR Policy. The complete policy of the SunSpec Alliance can be found at www.sunspec.org. Prepared by the SunSpec Alliance 4030 Moorpark Avenue, Suite 109 San Jose, CA 95117 Website: www.sunspec.org Email: info@sunspec.org

## Index
Model | Label | Description | Notes
801 | Energy Storage Base Model
802 | Battery Base Model
803 | Lithium-Ion Battery Model

## 801
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Energy Storage Base Model | 801 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 22 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | DERTyp | Distributed Energy Resource Type |  | enum16 |  |  | R | M | Type of distributed energy resource device.
Fixed Block |  | 3 | 1 | 1 | WHRtg | Nameplate Energy Capacity |  | uint16 | Wh | WHRtg_SF | R | M | Nameplate energy capacity in DC watt-hours.
Fixed Block |  | 4 | 2 | 1 | WMaxChaRte | Nameplate Max Charge Rate |  | uint16 | W | WMaxChaDisCha_SF | R | M | Maximum rate of energy transfer into the storage device.
Fixed Block |  | 5 | 3 | 1 | WMaxDisChaRte | Namplate Max Discharge Rate |  | uint16 | W | WMaxChaDisCha_SF | R | M | Maximum rate of energy transfer out of the storage device.
Fixed Block |  | 6 | 4 | 1 | DisChaRte | Self Discharge Rate |  | uint16 | %WHRtg | DisChaRte_SF | R | O | Self discharge rate. Percentage of capacity (WHRtg) discharged per day.
Fixed Block |  | 7 | 5 | 1 | SoCNpMaxPct | Nameplate Max SoC |  | uint16 | %WHRtg | SoC_SF | R | O | Manufacturer maximum state of charge, expressed as a percentage.
Fixed Block |  | 8 | 6 | 1 | SoCNpMinPct | Nameplate Min SoC |  | uint16 | %WHRtg | SoC_SF | R | O | Manufacturer minimum state of charge, expressed as a percentage.
Fixed Block |  | 9 | 7 | 1 | MaxRsvPct | Maximum Reserve Percent |  | uint16 | %WHRtg | SoC_SF | RW | O | Setpoint for maximum reserve for storage as a percentage of the nominal maximum storage.
Fixed Block |  | 10 | 8 | 1 | MinRsvPct | Minimum Reserve Percent |  | uint16 | %WHRtg | SoC_SF | RW | O | Setpoint for maximum reserve for storage as a percentage of the nominal maximum storage.
Fixed Block |  | 11 | 9 | 1 | SoC | State of Charge |  | uint16 | %WHRtg | SoC_SF | R | M | State of charge, expressed as a percentage. | Measurement
Fixed Block |  | 12 | 10 | 1 | ChaSt | ChaSt |  | enum16 |  |  | R | O | Charge status of storage device. Enumerated value.
Fixed Block |  | 13 | 11 | 1 | LocRemCtl | Control Mode |  | enum16 |  |  | R | M | DER control mode. Enumeration. | Maps to DRCC.LocRemCtl in 61850.
Fixed Block |  | 14 | 12 | 2 | Evt | Event Bitfield |  | bitfield32 |  |  | R | M | Bitmask value. Event fields.
Fixed Block |  | 16 | 14 | 1 | DERHb | Distributed Energy Resource Heartbeat |  | uint16 |  |  | RW | O | Value is incremented every second with periodic resets to zero.
Fixed Block |  | 17 | 15 | 1 | ControllerHb | Controller Heartbeat |  | uint16 |  |  | RW | O | Value is incremented every second with periodic resets to zero.
Fixed Block |  | 18 | 16 | 1 | DERAlarmReset | Alarm Reset |  | uint16 |  |  | R | O | Used to reset any latched alarms. 1 = Reset.
Fixed Block |  | 19 | 17 | Size: 1; Name: WHRtg_SF; Type: sunssf; R/W: R | M | Scale factor for energy capacity.
Fixed Block |  | 20 | 18 | Size: 1; Name: WMaxChaDisCha_SF; Type: sunssf; R/W: R | M | Scale factor for maximum charge and discharge rate.
Fixed Block |  | 21 | 19 | Size: 1; Name: DisChaRte_SF; Type: sunssf; R/W: R | O | Scale factor for self discharge rate.
Fixed Block |  | 22 | 20 | Size: 1; Name: SoC_SF; Type: sunssf; R/W: R | M | Scale factor for state of charge values.
Fixed Block |  | 23 | 21 | Size: 1; Name: Pad; Type: pad; R/W: R | M | Padding
enum16 | DERTyp |  |  | Name: STORAGE; Label: Storage Device; Value: 90 |  | A generic energy storage device. | Not yet a part of IEC 61850 DERTyp.
enum16 | DERTyp |  |  | Name: BATTERY; Label: Battery Device; Value: 91 |  | A generic battery. | Not yet a part of IEC 61850 DERTyp.
enum16 | DERTyp |  |  | Name: LITHIUM-ION BATTERY; Label: Lithium-ion Battery Device; Value: 92 |  | A lithium-ion battery. | Not yet a part of IEC 61850 DERTyp.
enum16 | DERTyp |  |  | Name: REDOX FLOW BATTERY; Label: Redox Flow Battery Device; Value: 93 |  | A redox flow battery. | Not yet a part of IEC 61850 DERTyp.
enum16 | ChaSt |  |  | Name: OFF; Value: 1
enum16 | ChaSt |  |  | Name: EMPTY; Value: 2
enum16 | ChaSt |  |  | Name: DISCHARGING; Value: 3
enum16 | ChaSt |  |  | Name: CHARGING; Value: 4
enum16 | ChaSt |  |  | Name: FULL; Value: 5
enum16 | ChaSt |  |  | Name: HOLDING; Value: 6
enum16 | ChaSt |  |  | Name: TESTING; Value: 7
enum16 | LocRemCtl |  |  | Name: REMOTE; Label: Remote Control; Value: 1 |  | Battery is controlled remotely (e.g. by the site controller). | Value of 0 matches LocRemCtl in 61850.
enum16 | LocRemCtl |  |  | Name: LOCAL; Label: Local Control; Value: 2 |  | Battery is controlled by a local operator (e.g. through battery HMI). | Value of 1 matches LocRemCtl in 61850.
bitfield32 | Evt |  |  | Name: UNDER_SOC_MIN_WARNING; Label: Under State of Charge Minimum Warning; Value: 0 |  | Battery state of charge is approaching SoCNpMinPct
bitfield32 | Evt |  |  | Name: UNDER_SOC_MIN_ALARM; Label: Under State of Charge Minimum Alarm; Value: 1 |  | Battery state of charge has reached or exceeded SoCNpMinPct
bitfield32 | Evt |  |  | Name: OVER_SOC_MAX_WARNING; Label: Over State of Charge Maximum Warning; Value: 2 |  | Battery state of charge is approaching SoCNpMaxPct
bitfield32 | Evt |  |  | Name: OVER_SOC_MAX_ALARM; Label: Over State of Charge Maximum Warning; Value: 3 |  | Battery state of charge has reached or exceeded SocNpMaxPct

## 802
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Battery Base Model | 802 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 20 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | BatTyp | Battery Type |  | enum16 |  |  | R | M | Type of battery. Enumeration. | Maps to DBAT in 61850.
Fixed Block |  | 3 | 1 | 1 | BatSt | State of the Battery Bank |  | enum16 |  |  | R | M | State of the battery bank. Enumeration. | Must be reconciled with BatSt in IEC 61850.
Fixed Block |  | 4 | 2 | 2 | CycleCt | Cycle Count |  | uint32 |  |  | R | O | Number of cycles executed in the battery.
Fixed Block |  | 6 | 4 | 1 | SoH | State of Health |  | uint16 | % | SoH_SF | R | O | Percentage of battery life remaining.
Fixed Block |  | 7 | 5 | 2 | Evt1 | Battery Event 1 Bitfield |  | bitfield32 |  |  | R | M | Alarms and warnings. Bit flags.
Fixed Block |  | 9 | 7 | 2 | Evt2 | Battery Event 2 Bitfield |  | bitfield32 |  |  | R | M | Alarms and warnings. Bit flags. | Reserved for future use.
Fixed Block |  | 11 | 9 | 1 | Vol | External Battery Voltage |  | uint16 | V | Vol_SF | R | M | DC Bus Voltage | Measurement. Maps to ZBAT.Vol.
Fixed Block |  | 12 | 10 | 1 | MaxBatACha | Max Charge Current |  | uint16 | A | MaxBatA_SF | R | M | Instantaneous maximum DC charge current. | Calculation. Nearly maps to ZBAT.MaxBatA.
Fixed Block |  | 13 | 11 | 1 | MaxBatADischa | Max Discharge Current |  | uint16 | A | MaxBatA_SF | R | M | Instantaneous maximum DC discharge current. | Calculation. Nearly maps to ZBAT.MaxBatA.
Fixed Block |  | 14 | 12 | 1 | BatReqPCSSt | PCS State Request |  | enum16 |  |  | R | O | Request from battery to start or stop the PCS. Enumeration. | Used in special states such as manual battery charging.
Fixed Block |  | 15 | 13 | 1 | BatReqW | Battery Power Request |  | int16 | W | BatReqW_SF | R | O | AC Power requested by battery. | Used in special states such as string balancing.
Fixed Block |  | 16 | 14 | 1 | BSetOperation | Set Operation |  | enum16 |  |  | RW | M | Instruct the battery bank to perform an operation such as connecting. Enumeration.
Fixed Block |  | 17 | 15 | 1 | BSetPCSState | PCS State |  | enum16 |  |  | RW | M | PCS State | Information needed by battery for some operations.
Fixed Block |  | 18 | 16 | Size: 1; Name: SoH_SF; Type: sunssf; R/W: R | O | Scale factor for State of Health.
Fixed Block |  | 19 | 17 | Size: 1; Name: Vol_SF; Type: sunssf; R/W: R | M | Scale factor for DC Bus Voltage.
Fixed Block |  | 20 | 18 | Size: 1; Name: MaxBatA_SF; Type: sunssf; R/W: R | M | Scale factor for instantationous DC charge/discharge current.
Fixed Block |  | 21 | 19 | Size: 1; Name: BatReqW_SF; Type: sunssf; R/W: R | O | Scale factor for AC power request.
enum16 | BatTyp |  |  | Name: NOT APPLICABLE_UNKNOWN; Label: Not Applicable or Unknown; Value: 0 |  | Battery type is not applicable or unknown.
enum16 | BatTyp |  |  | Name: LEAD_ACID; Label: Lead-Acid; Value: 1 |  | Lead-acid battery type.
enum16 | BatTyp |  |  | Name: NICKEL_METAL_HYDRATE; Label: Nickel-Metal Hydrate; Value: 2 |  | Nickel-metal hydrate battery type.
enum16 | BatTyp |  |  | Name: NICKEL_CADMIUM; Label: Nickel-Cadmium; Value: 3 |  | Nickel-cadmium battery type.
enum16 | BatTyp |  |  | Name: LITHIUM_ION; Label: Lithium-Ion; Value: 4 |  | Lithium-ion battery type.
enum16 | BatTyp |  |  | Name: CARBON_ZINC; Label: Carbon-Zinc; Value: 5 |  | Carbon-zinc battery type.
enum16 | BatTyp |  |  | Name: ZINC_CHLORIDE; Label: Zinc Chloride; Value: 6 |  | Zinc chloride battery type.
enum16 | BatTyp |  |  | Name: ALKALINE; Label: Alkaline; Value: 7 |  | Alkaline battery type.
enum16 | BatTyp |  |  | Name: RECHARGEABLE_ALKALINE; Label: Rechargeable Alkaline; Value: 8 |  | Rechargeable alkaline battery type.
enum16 | BatTyp |  |  | Name: SODIUM_SULFUR; Label: Sodium-Sulfur; Value: 9 |  | Sodium-sulfur battery type.
enum16 | BatTyp |  |  | Name: FLOW; Label: Flow; Value: 10 |  | Flow battery type.
enum16 | BatTyp |  |  | Name: OTHER; Label: Other; Value: 99 |  | Other battery type.
enum16 | BatSt |  |  | Name: DISCONNECTED; Label: Disconnected; Value: 1 |  | Battery bank is disconnected. All contactors are open.
enum16 | BatSt |  |  | Name: INITIALIZING; Label: Initializing; Value: 2 |  | Battery bank is initializing but not ready for operating. String balancing may occur.
enum16 | BatSt |  |  | Name: CONNECTED; Label: Connected; Value: 3 |  | Battery bank is ready for operation. All enabled contactors are closed.
enum16 | BatSt |  |  | Name: STANDBY; Label: Standby; Value: 4 |  | Battery bank is connected and in standby/power saving mode.
enum16 | BatSt |  |  | Name: SOC PROTECTION; Label: SOC Protection; Value: 5 |  | Battery bank is connected but SOC is too low. Battery should be considered "offline".
bitfield32 | Evt1 |  |  | Name: COMMUNICATION_ERROR; Label: Communication Error; Value: 0 |  | Unable to communcate with BMS or BMS is unable to communicate with battery strings.
bitfield32 | Evt1 |  |  | Name: OVER_TEMP_ALARM; Label: Over Temperature Alarm; Value: 1 |  | Battery has exceeded maximum operating temperature
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP_ALARM; Label: Under Temperature Alarm; Value: 2 |  | Battery has exceeded minimum operating temperature
bitfield32 | Evt1 |  |  | Name: OVER_TEMP_WARNING; Label: Over Temperature Warning; Value: 3 |  | Battery is approaching maximum operating temperature.
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP_WARNING; Label: Under Temperature Warning; Value: 4 |  | Battery is approaching minimum operating temperature.
bitfield32 | Evt1 |  |  | Name: OVER_CHARGE_CURRENT_ALARM; Label: Over Charge Current Alarm; Value: 5 |  | Battery maximum charge current has been exceeded. | See AMaxCha
bitfield32 | Evt1 |  |  | Name: OVER_DISCHARGE_CURRENT_ALARM; Label: Over Discharge Current Alarm; Value: 6 |  | Battery maximum discharge current has been exceeded. | See AMaxDischa
bitfield32 | Evt1 |  |  | Name: OVER_CHARGE_CURRENT_WARNING; Label: Over Charge Current Warning; Value: 7 |  | Approaching battery maximum charge current. | See AMaxCha
bitfield32 | Evt1 |  |  | Name: OVER_DISCHARGE_CURRENT_WARNING; Label: Over Discharge Current Warning; Value: 8 |  | Approaching battery maximum discharge current. | See AMaxDischa
bitfield32 | Evt1 |  |  | Name: VOLTAGE_IMBALANCE_WARNING; Label: Voltage Imbalance Warning; Value: 9 |  | A voltage imbalance exists between the strings in the battery bank.
bitfield32 | Evt1 |  |  | Name: CURRENT_IMBALANCE_WARNING; Label: Current Imbalance Warning; Value: 10 |  | A current imbalance exists between the strings in the battery bank.
bitfield32 | Evt1 |  |  | Name: OVER_VOLT_ALARM; Label: Over Voltage Alarm; Value: 11 |  | Battery voltage has exceeded maximum limit.
bitfield32 | Evt1 |  |  | Name: UNDER_VOLT_ALARM; Label: Under Voltage Alarm; Value: 12 |  | Battery voltage has exceeded minimum limit.
bitfield32 | Evt1 |  |  | Name: OVER_VOLT_WARNING; Label: Over Voltage Warning; Value: 13 |  | Battery voltage is approaching maximum limit.
bitfield32 | Evt1 |  |  | Name: UNDER_VOLT_WARNING; Label: Under Voltage Warning; Value: 14 |  | Battery voltage is approaching minimum limit.
bitfield32 | Evt1 |  |  | Name: CONTACTOR_ERROR; Label: Contactor Error; Value: 15 |  | A contactor failed to open or close as requested.
bitfield32 | Evt1 |  |  | Name: FAN_ERROR; Label: Fan Error; Value: 16 |  | One or more battery fans has failed.
bitfield32 | Evt1 |  |  | Name: CONTACTOR_STATUS; Label: Contactor Status; Value: 17 |  | String contactor is closed.
bitfield32 | Evt1 |  |  | Name: GROUND_FAULT; Label: Ground Fault Error; Value: 18 |  | Ground fault detected.
bitfield32 | Evt1 |  |  | Name: OPEN_DOOR_ERROR; Label: Open Door Error; Value: 19 |  | One or more door are open.
bitfield32 | Evt1 |  |  | Name: OTHER_ALARM; Label: Other Battery Alarm; Value: 20 |  | For manufacturer-specific alarms.
bitfield32 | Evt1 |  |  | Name: OTHER_WARNING; Label: Other Battery Warning; Value: 21 |  | For manufacturer-specific warnings.
enum16 | BatReqPCSSt |  |  | Name: NO REQUEST; Label: No Request; Value: 0 |  | Battery has no requests of the PCS.
enum16 | BatReqPCSSt |  |  | Name: START; Label: Start PCS; Value: 1 |  | Battery requests that the PCS be started. | Battery is notified of PCS state change through BSetPcsState.
enum16 | BatReqPCSSt |  |  | Name: STOP; Label: Stop PCS; Value: 2 |  | Battery requests that the PCS be stopped. | Battery is notified of PCS state change through BSetPcsState.
enum16 | BSetOperation |  |  | Name: CONNECT; Label: Connect the Battery Bank; Value: 1 |  | Initialize the battery bank and close contactors for all enabled strings.
enum16 | BSetOperation |  |  | Name: DISCONNECT; Label: Disconnect the Battery Bank; Value: 2 |  | Open contactors for all strings.
enum16 | BSetPCSState |  |  | Name: PCS_STOPPED; Label: PCS is Stopped; Value: 1
enum16 | BSetPCSState |  |  | Name: PCS_STANDBY; Label: PCS is in Standby; Value: 2
enum16 | BSetPCSState |  |  | Name: PCS_STARTED; Label: PCS is Started; Value: 3

## 803
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Lithium-Ion Battery Model | 803 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 16 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | BConStrCt | Connected String Count |  | uint16 |  |  | R | M | Number of strings with contactor closed.
Fixed Block |  | 3 | 1 | 1 | BMaxCellVol | Max Cell Voltage |  | uint16 | V | BCellVol_SF | R | M | Maximum voltage for all cells in the bank. | Measurement
Fixed Block |  | 4 | 2 | 1 | BMaxCellVolLoc | Max Cell Voltage Location |  | uint16 |  |  | R | O | Location of the cell with maximum voltage | Bit0:Bit7 = String Number Bit8:Bit15 = Module Number
Fixed Block |  | 5 | 3 | 1 | BMinCellVol | Min Cell Voltage |  | uint16 | V | BCellVol_SF | R | M | Minimum voltage for all cells in the bank. | Measurement
Fixed Block |  | 6 | 4 | 1 | BMinCellVolLoc | Min Cell Voltage Location |  | uint16 |  |  | R | O | Location of the cell with minimum voltage | Bit0:Bit7 = String Number Bit8:Bit15 = Module Number
Fixed Block |  | 7 | 5 | 1 | BMaxModTmp | Max Module Temp |  | int16 |  | BModTmp_SF | R | M | Maximum temperature for all modules in the bank. | Measurement
Fixed Block |  | 8 | 6 | 1 | BMaxModTmpLoc | Max Module Temp Location |  | uint16 |  |  | R | O | Location of the module with max temperature. | Bit0:Bit7 = String Number Bit8:Bit15 = Module Number
Fixed Block |  | 9 | 7 | 1 | BMinModTmp | Min Module Temp |  | int16 | C | BModTmp_SF | R | M | Minimum temperature for all modules in the bank. | Measurement
Fixed Block |  | 10 | 8 | 1 | BMinModTmpLoc | Min Module Temp Location |  | uint16 |  |  | R | O | Location of the module with min temperature. | Bit0:Bit7 = String Number Bit8:Bit15 = Module Number
Fixed Block |  | 11 | 9 | 1 | BTotDCCur | Total DC Current |  | int16 | A | BCurrent_SF | R | M | Total DC current flowing to/from the battery bank. | Measurement
Fixed Block |  | 12 | 10 | 1 | BMaxStrCur | Max String Current |  | int16 | A | BCurrent_SF | R | O | Maximum current of any string in the bank. | Measurement
Fixed Block |  | 13 | 11 | 1 | BMinStrCur | Min String Current |  | int16 | A | BCurrent_SF | R | O | Minimm current of any string in the bank. | Measurement
Fixed Block |  | 14 | 12 | Size: 1; Name: BCellVol_SF; Type: sunssf; R/W: R | M | Scale factor for cell voltage.
Fixed Block |  | 15 | 13 | Size: 1; Name: BModTmp_SF; Type: sunssf; R/W: R | M | Scale factor for module temperatures.
Fixed Block |  | 16 | 14 | Size: 1; Name: BCurrent_SF; Type: sunssf; R/W: R | M | Scale factor for Total DC Current, Max String Current and Min String Current.
Fixed Block |  | 17 | 15 | Size: 1; Name: StrSoH_SF; Type: sunssf; R/W: R | O | Scale factor for String State of Health.
Repeating Block |  | 18 | 0 | 1 | StrModCt | Module Count |  | uint16 |  |  | R | M | Count of modules in the string.
Repeating Block |  | 19 | 1 | 1 | StrSoC | String SoC |  | uint16 | % |  | R | M | Battery string state of charge, expressed as a percentage. | Measurement
Repeating Block |  | 20 | 2 | 1 | StrSoH | String SoH |  | uint16 | % | StrSoH_SF | R | O | Battery string state of health, expressed as a percentage. | Measurement
Repeating Block |  | 21 | 3 | 1 | StrCur | String Current |  | int16 | A | BCurrent_SF | R | M | String current measurement. | Measurement
Repeating Block |  | 22 | 4 | 1 | StrMaxCellVol | Max Cell Voltage |  | uint16 | V | BCellVol_SF | R | M | Maximum voltage for all cells in the string. | Measurement
Repeating Block |  | 23 | 5 | 1 | StrMinCellVol | Min Cell Voltage |  | uint16 | V | BCellVol_SF | R | M | Minimum voltage for all cells in the string. | Measurement
Repeating Block |  | 24 | 6 | 1 | StrCellVolLoc | Max/Min Cell Voltage Loc |  | uint16 |  |  | R | O | Location of maximum and minimum cell voltages. | Bit0:Bit7 = Max Module Num Bit8:Bit15 = Min Module Num
Repeating Block |  | 25 | 7 | 1 | StrMaxModTmp | Max Module Temp |  | int16 | C | BModTmp_SF | R | M | Maximum temperature for all modules in the bank. | Measurement
Repeating Block |  | 26 | 8 | 1 | StrMinModTmp | Min Module Temp |  | int16 | C | BModTmp_SF | R | M | Minimum temperature for all modules in the bank. | Measurement
Repeating Block |  | 27 | 9 | 1 | StrModTmpLoc | Max/Min Mod Temp Loc |  | uint16 |  |  | R | O | Location of maximum and minimum module temperatures. | Bit0:Bit7 = Max Module Num Bit8:Bit15 = Min Module Num
Repeating Block |  | 28 | 10 | 2 | StrEvt1 | String Event 1 |  | bitfield32 |  |  | R | M | Alarms, warnings and status values. Bit flags.
Repeating Block |  | 30 | 12 | 2 | StrEvt2 | String Event 2 |  | bitfield32 |  |  | R | O | Alarms, warnings and status values. Bit flags. | Reserved for future use.
Repeating Block |  | 32 | 14 | 1 | StrConFail | Connection Failure Reason |  | enum16 |  |  | R | O
Repeating Block |  | 33 | 15 | 1 | StrSetEna | Enable/Disable String |  | enum16 |  |  | RW | O | Enables and disables the string. Should reset to 0 upon completion.
bitfield32 | StrEvt1 |  |  | Name: COMMUNICATION_ERROR; Label: Communication Error; Value: 0 |  | Unable to communcate with BMS.
bitfield32 | StrEvt1 |  |  | Name: OVER_TEMP_ALARM; Label: Over Temperature Alarm; Value: 1 |  | Battery string has exceeded maximum operating temperature.
bitfield32 | StrEvt1 |  |  | Name: UNDER_TEMP_ALARM; Label: Under Temperature Alarm; Value: 2 |  | Battery string has exceeded minimum operating temperature.
bitfield32 | StrEvt1 |  |  | Name: OVER_TEMP_WARNING; Label: Over Temperature Warning; Value: 3 |  | Battery string is approaching maximum operating temperature.
bitfield32 | StrEvt1 |  |  | Name: UNDER_TEMP_WARNING; Label: Under Temperature Warning; Value: 4 |  | Battery string is approaching minimum operating temperature.
bitfield32 | StrEvt1 |  |  | Name: OVER_CHARGE_CURRENT_ALARM; Label: Over Charge Current Alarm; Value: 5 |  | Battery string maximum charge current has been exceeded. | See AMaxCha
bitfield32 | StrEvt1 |  |  | Name: OVER_DISCHARGE_CURRENT_ALARM; Label: Over Discharge Current Alarm; Value: 6 |  | Battery string maximum discharge current has been exceeded. | See AMaxDischa
bitfield32 | StrEvt1 |  |  | Name: OVER_CHARGE_CURRENT_WARNING; Label: Over Charge Current Warning; Value: 7 |  | Approaching battery string maximum charge current. | See AMaxCha
bitfield32 | StrEvt1 |  |  | Name: OVER_DISCHARGE_CURRENT_WARNING; Label: Over Discharge Current Warning; Value: 8 |  | Approaching battery string maximum discharge current. | See AMaxDischa
bitfield32 | StrEvt1 |  |  | Name: OVER_VOLT_ALARM; Label: Over Voltage Alarm; Value: 9 |  | Battery string voltage has exceeded maximum limit.
bitfield32 | StrEvt1 |  |  | Name: UNDER_VOLT_ALARM; Label: Under Voltage Alarm; Value: 10 |  | Battery string voltage has exceeded minimum limit.
bitfield32 | StrEvt1 |  |  | Name: OVER_VOLT_WARNING; Label: Over Voltage Warning; Value: 11 |  | Battery string voltage is approaching maximum limit.
bitfield32 | StrEvt1 |  |  | Name: UNDER_VOLT_WARNING; Label: Under Voltage Warning; Value: 12 |  | Battery string voltage is approaching minimum limit.
bitfield32 | StrEvt1 |  |  | Name: CONTACTOR_ERROR; Label: Contactor Error; Value: 13 |  | String contactor failed to open or close as requested.
bitfield32 | StrEvt1 |  |  | Name: FAN_ERROR; Label: Fan Error; Value: 14 |  | Battery string fan has failed.
bitfield32 | StrEvt1 |  |  | Name: CONTACTOR_STATUS; Label: Contactor Status; Value: 15 |  | String contactor is closed.
bitfield32 | StrEvt1 |  |  | Name: GROUND_FAULT; Label: Ground Fault Error; Value: 16 |  | Ground fault detected.
bitfield32 | StrEvt1 |  |  | Name: OPEN_DOOR_ERROR; Label: Open Door Error; Value: 17 |  | One or more door are open.
bitfield32 | StrEvt1 |  |  | Name: OTHER_ALARM; Label: Other Alarm; Value: 18 |  | An alarm has been triggered which does not map to one of the alarms above. | Operator should view battery HMI and/or logs for more information.
bitfield32 | StrEvt1 |  |  | Name: OTHER_WARNING; Label: Other Warning; Value: 19 |  | A warning has been triggered which does not map to one of the alarms above. | Operator should view battery HMI and/or logs for more information.
bitfield32 | StrEvt1 |  |  | Name: STRING_ENABLED; Label: String Enabled; Value: 20 |  | The string is currently enabled.
enum16 | StrConFail |  |  | Name: NO FAILURE; Value: 0 |  | Connect did not fail.
enum16 | StrConFail |  |  | Name: BUTTON_PUSHED; Value: 1 |  | A button was pushed which prevented connection.
enum16 | StrConFail |  |  | Name: STR_GROUND_FAULT; Value: 2 |  | Ground fault during auto-connect.
enum16 | StrConFail |  |  | Name: OUTSIDE_VOLTAGE_RANGE; Value: 3 |  | Outside voltage target window during auto-connect.
enum16 | StrSetEna |  |  | Name: ENABLE; Value: 1 |  | Enable the string.
enum16 | StrSetEna |  |  | Name: DISABLE; Value: 2 |  | Disable the string.